## TEASER_sizing
Neighbourhood | Boxbergheide | OudWinterslag | TermienEast | TermienWest | WaterscheiGarden | Winterslag | ZwartbergNEast | ZwartbergNWest | ZwartbergSouth | F+H | dist_pipe13 | dist_pipe12 | dist_pipe11 | dist_pipe10 | dist_pipe9 | dist_pipe8 | dist_pipe7 | dist_pipe6 | dist_pipe5 | dist_pipe4 | dist_pipe3 | dist_pipe2 | dist_pipe1 | dist_pipe0
Number of buildings | 1753 | 360 | 414 | 455 | 1491 | 1313 | 500 | 410 | 1079 | 1991 | 455 | 414 | 869 | 1313 | 1753 | 3935 | 360 | 4295 | 1079 | 410 | 5784 | 1491 | 500 | 7775
Max mass flow rate [kg/s] | 279.1846 | 57.334 | 65.9341 | 72.4638 | 237.4582 | 209.1097 | 79.6305 | 65.297 | 171.8427 | 317.0887 | 72.4638 | 65.9341 | 138.3978 | 209.1097 | 279.1846 | 626.6921 | 57.334 | 684.0261 | 171.8427 | 65.297 | 921.1658 | 237.4582 | 79.6305 | 1238.2545
Max mass flow rate [m^3/h] | 1005.0645 | 206.4023 | 237.3626 | 260.8696 | 854.8495 | 752.795 | 286.6699 | 235.0693 | 618.6335 | 1141.5194 | 260.8696 | 237.3626 | 498.2322 | 752.795 | 1005.0645 | 2256.0917 | 206.4023 | 2462.494 | 618.6335 | 235.0693 | 3316.1968 | 854.8495 | 286.6699 | 4457.7162
DN | 350 | 200 | 200 | 200 | 350 | 300 | 200 | 200 | 300 | 400 | 200 | 200 | 250 | 300 | 350 | 500 | 200 | 500 | 300 | 200 | 600 | 350 | 200 | 600
Max power of one substation [W] | 20000
Average delta T across HEx [K] | 30

## mass flow rates
DN | Max mass flow rate [m^3/h]
20 | 1.547
25 | 2.526
32 | 4.695
40 | 6.303
50 | 11.757
65 | 19.563
80 | 30.791
100 | 51.891
125 | 89.35
150 | 152.573
200 | 299.541
250 | 539.4
300 | 847.85
350 | 1092.75
400 | 1550
450 | 2123.5
500 | 2821
600 | 4526
700 | 6773.5
800 | 9672
900 | 14725
1000 | 21700